## Sheet1
This spreadsheet is intended to be a guide only. ALWAYS REFERENCE THE BPI BUILDING ANALYST STANDARD.
Either digital versions or scanned field forms are acceptable. For Apartments with Multiple CAZ/CVA Requirements or Equipment Enter Data on Next Column.
Location Info | Unit #
| CO Monitor Installed? | Yes/Pass No/Fail | Yes/Pass No/Fail
Ambient CO (Pre-Testing ppm)
| Ambient CO Under 35 ppm? | Yes/Pass No/Fail | Yes/Pass No/Fail
Gas Oven | Gas line test - Circle Result | Pass Fail | Pass Fail
Oven CO (ppm)
| Oven CO (ppm) - Circle Result | Below 100 ppm/Pass Between 101-300 ppm/Pass - Recommend Service Above 300 ppm and exhaust rate < 100 CFM/Fail | Below 100 ppm/Pass Between 101-300 ppm/Pass - Recommend Service Above 300 ppm and exhaust rate < 100 CFM/Fail
Ambient CO during testing (ppm)
| Ambient CO Under 35 ppm? | Yes/Pass No/Fail | Yes/Pass No/Fail
Combustion Ventilation Area | Area Volume (cu ft)
Total Combined BTU Input
CVA Required (<50 CF/1000 BTU)?
Existing NFV Area/Opening High (sq in)
Existing NFV Area/Opening Low (sq in)
| Does CVA meet NFPA 54 Code Requirement? | Yes/Pass No/Fail | Yes/Pass No/Fail
WC Test | Base Pressure (Pa)
Worst Case Pressure (Pa)
Net Depressurization (Pa)
| CAZ Depressurization Limit Exceeded? | No/Pass Yes/Fail | No/Pass Yes/Fail
General Equipment Information | Equipment Type
Model #
| Gas line test | Pass Fail | Pass Fail
| Flue Inspection | Pass Fail | Pass Fail
Equip. depressurization limit (pa)
Required Minimum Draft (pa)
Worst Case | Worst Case:Spillage Stops before 1 minute | Yes/Pass No/Test Natural | Yes/Pass No/Test Natural
Worst Case: pre-dilution CO in flue (ppm)
| Worst Case: pre-dilution CO in flue (ppm) - Circle One | Below 26 ppm/Pass Between 26-100 ppm/Pass - Recommend Service Over 100 ppm/Fail | Below 26 ppm/Pass Between 26-100 ppm/Pass - Recommend Service Over 100 ppm/Fail
Worst Case: Draft (pa)
| Worst Case: Draft (pa) - Circle Result | Pass Test Natural | Pass Test Natural
| Pass WC Test? | Yes/Pass No/Test Natural | Yes/Pass No/Test Natural
Natural | Natural: Spillage Stops before 1 minute | Yes/Pass No/Fail | Yes/Pass No/Fail
Natural: pre-dilution CO in flue (ppm)
| Natural: pre-dilution CO in flue (ppm) - Circle Result | Below 26 ppm/Pass Between 26-100 ppm/Pass - Recommend Service Over 100 ppm/Fail | Below 26 ppm/Pass Between 26-100 ppm/Pass - Recommend Service Over 100 ppm/Fail
Natural: Draft (pa)
| Natural: Draft (pa) - Circle Result | Pass Fail | Pass Fail
| Pass Natural Test? | Pass Fail | Pass Fail
RESULT | OVERALL TEST RESULTS FOR THIS UNIT (Any FAILS circled above constitute failure) | Pass Fail | Pass Fail
NOTES
Note on A7: Per the BPI Gold Sheet: 1. Remove any items/foil in or on oven/range top. 2. Make sure self-cleaning features are not activated. 3. Test oven in vent sleeve, before dilution air. 4. 100 ppm to 300 ppm as measured you must install a carbon monoxide detector and recommendation for service must be made to the consumer. Greater than 300 ppm as measured—the unit must be serviced prior to work. If greater than 300 ppm after servicing, exhaust ventilation must be provided with a capacity of 25 CFM continuous or 100 CFM intermittent. A failure for the ovens is either CO levels of above 300 ppm measured in the oven or ambient CO levels of 25 ppm or more.
Note on A18: Per the BPI Gold Sheet: 1. Measure the Base Pressure. Start with all exterior doors and windows closed and the fireplace damper closed. Set all combustion appliances to the pilot setting or turn off the service disconnect. Combustion appliances include: boiler, furnace, space-heaters, and water heater. With the home in this configuration, measure and record the baseline pressure of the mechanical room WRT outside. 2. Establish the Worst Case. Turn on the dryer and all exhaust fans. Close all interior doors that make the CAZ pressure more negative. Turn on the air handler, if present, and leave on if the pressure in the CAZ becomes more negative, then recheck the door positions. Measure the net change in pressure from the CAZ to outside, correcting for the base pressure. Record the “worst case depressurization” and compare to the CAZ Depressurization Limit Table.
Note on A22: Per the BPI Gold Sheet: 3. Measure Worst Case Spillage, Draft, CO. Fire the appliance with the smallest Btu capacity first, test for spillage at the draft diverter with a mirror or smoke test, and test for the CO at the flue at steady-state (if steady state is not achieved within 10 minutes, take the CO readings at the 10 minute mark). If the spillage test fails under worst case, go to Step 4. If spillage ends within 1 minute, test the draft in the connector 1’ - 2’ after the diverter or first elbow. Fire all other connected appliances simultaneously and test the draft diverter of each appliance for spillage. Test for CO in all appliances before the draft diverter. 4. Measure Spillage, Draft, CO under Natural Conditions. If spillage fails under worst case, turn off the appliance, the exhaust fans, open the interior doors and allow the vent to cool before re-testing. Test for CO, spillage, and draft under “natural conditions.” Measure the net change in pressure from worst case to natural in the CAZ to confirm the “worst case depressurization” taken in Step 2 outside. Repeat the process for each appliance, allowing the vent to cool between tests. 5. Ambient CO. Monitor the ambient CO in the breathing zone during the test procedure and abort the test if ambient CO goes over 35 ppm. Turn off the appliance, ventilate the space, and evacuate the building. The building may be reentered once ambient CO levels have gone below 35 ppm. The appliance must be repaired and the problem corrected prior to completing the combustion safety diagnostics. If the ambient levels exceed 35 ppm during testing under natural conditions, disable the appliance and instruct the homeowner to have the appliance repaired prior to operating it again. 6. Action Levels. Make recommendations or complete work order for repairs based on test results and the Combustion Safety Test Action Level Tables.